Date of Joint:

| Joint location / SS Name |  | Contractor name |  |
| --- | --- | --- | --- |
| Conductor (AL / Cu) |  | Contract /PO No |  |
| Cable size and voltage |  | Scheme No. / WO No. |  |
| Joint Manufacturer |  | Coordinates |  |

New Joint (First joint)                                                                   New Joint  (Replacement to the failed joint)

| SN | Content | YES | NO | NA | Remark |
| --- | --- | --- | --- | --- | --- |
| 1 | Documents such as NOCs, Approved method statement, risk assessment, route layout to be available at site. |  |  |  |  |
| 2 | Valid Competency of the jointer. |  |  |  |  |
| 3 | End cap to be available at the cable ends (IN case of not connected ). |  |  |  |  |
| 4 | Adequate loop to be kept at the joint location. |  |  |  |  |
| 5 | All necessary & and recommended tools with calibration required for the job. |  |  |  |  |
| 6 | Failed joint / failed portion of the cable is removed? |  |  |  |  |
| 7 | Manufacture instruction booklet available and read. |  |  |  |  |
| 8 | All tubes, ferrules and accessories required are available with the kit. |  |  |  |  |
| 9 | Cable ends preparation for joint as per manufacturer manual. |  |  |  |  |
| 10 | Do not use Knife to remove semi-conductor layer |  |  |  |  |
| 11 | Conductor length and insulation removal as per installation instructions. |  |  |  |  |
| 12 | Phase checking and crimping ferrules. |  |  |  |  |
| 13 | Sharp edges of broken bolts and ferrules are properly smoothened. Cleaning of ferrules. |  |  |  |  |
| 14 | Void fillers were applied as applicable. |  |  |  |  |
| 15 | Stress control tube to be provided. |  |  |  |  |
| 16 | Armored and outer jacket to be provided. |  |  |  |  |
| 17 | Jointer tag to be provided. |  |  |  |  |
| 18 | Required photos as proof are collected. |  |  |  |  |
| 19 | Ensure Insulation resistance and VLF is performed. |  |  |  |  |

Note: The preparation of the joint should adhere to the manufacturer's guidelines, this checklist is intended solely to verify the implementation of key areas.

| Contractor Representative |  | Supervision Team |  |
| --- | --- | --- | --- |
| Name / ID |  | Name |  |
| Signature |  | Signature |  |