Date of Termination: 18-02-2025

| Termination location | Aljimi | Contractor name | Time Electro |
| --- | --- | --- | --- |
| SS name | JM-0340 | Contract /PO No | A-18392 |
| Conductor (AL / Cu) | AL | Scheme No. / WO No. | ND-11-24-085 |
| Cable size and voltage | 400 sq.mm | Termination Manufacturer | Raychem |

y

New Termination (First termination)                      New termination  (Replacement to the failed termination)

| SN | Content | YES | NO | NA | Remark |
| --- | --- | --- | --- | --- | --- |
| 1 | Documents such as NOCs, Approved method statement, risk assessment, route layout to be available at site. | Y |  |  |  |
| 2 | Valid Competency of the jointer. | Y |  |  |  |
| 3 | Adequate 2 meters of loop available outside substation. | Y |  |  |  |
| 4 | End cap to be available at the cable ends (IN case of not connected). | Y |  |  |  |
| 5 | Manufacture instruction booklet available and read. | Y |  |  |  |
| 6 | Preparation of cable end as per manufacturer manual. | Y |  |  |  |
| 7 | All necessary & recommended tools with calibration required for the job. | Y |  |  |  |
| 8 | All accessories required are available with the kit. | Y |  |  |  |
| 9 | Do not use Knife to remove semi-conductor layer | Y |  |  |  |
| 10 | Conductor length and insulation removal as per installation instructions. | Y |  |  |  |
| 11 | All 3 cores should be straightening V shape. | Y |  |  |  |
| 12 | No sharp edges of crimped lugs. | Y |  |  |  |
| 13 | Sand/dust/moisture is cleaned from lugs and tubes. | Y |  |  |  |
| 14 | The stress control tube and stress control patch are located properly and shrunk without any wrinkles. | Y |  |  |  |
| 15 | Cable should be properly clamped. | Y |  |  |  |
| 16 | Cable tag is to be provided for the termination. | Y |  |  |  |
| 17 | Required photos as proof are collected. | Y |  |  |  |
| 18 | Ensure Insulation resistance and VLF is performed. | y |  |  |  |

Note: The preparation of the termination should adhere to the manufacturer's guidelines, this checklist is intended solely

to verify the implementation of key areas.

| Contractor Representative |  | Supervision Team |  |
| --- | --- | --- | --- |
| Name / ID | Saiful Islam Khan | Name | Hamad Sultan |
| Signature |  | Signature |  |